| رقم البند | اسم المادة ومواصفاتها |  | الوحدة | الكمية المطلوبة | الماركة | المنشأ | مدة التسليم | الأسعار بالدينار الأردني |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  |  |  | السعر الإفرادي |  | السعر الإجمالي |  |
|  |  |  |  |  |  |  |  | ف | د | ف | د |
| 1 | Power hardware in the loop based microgrid testbench that contains the following 4 items: | 1. Real-time network simulator (RTNS) | عدد | 1 |  |  |  |  |  |  |  |
|  |  | 2.Software license to run the models | عدد | 1 |  |  |  |  |  |  |  |
|  |  | 3.Distributed Energy Resources (DER) Emulator | عدد | 3 |  |  |  |  |  |  |  |
|  |  | 4.Grid Emulator PHIL | عدد | 1 |  |  |  |  |  |  |  |
| 2 | Desktop PCs For data acquisition and system monitoring |  | عدد | 3 |  |  |  |  |  |  |  |

المواصفات الفنية الدقيقة لكل مادة تابعة لنظام المحاكي المطلوب موضحة حسب الجدول التالي :-

| البند (الأجهزة) Item (Equipment) | الوصف Description | العدد |
| --- | --- | --- |
| Real-time network simulator (RTNS) | - The RTNS must offer computation capability in order to run power systems models in real- time - The real-time simulator must offer a set of standard I/Os (Analogue Input-output channels, [-15 V; + 15 V], 16-bits resolution, Digital Input-output channels (0-30 V) - The RTNS must be controlled by dedicated software modules define and manage the simulation environment. These software modules include the real-time operating system and a function to convert Simulink models into an executable simulator model file. - The modeling environment must be based on Matlab/Simulink. - The modeling environment must involve dynamic simulation of power systems in phasor mode and be used for the testing and integration of energy management systems. - The System must be able to simulate microgrid models with 500 buses in minimum at 10 ms in real-time. - The system must include a set of models ready to be used: - Grid model / Microgrid Model - Distributed Energy Resources models. These Distributed Energy Resources can represent: - Wind turbine - Solar system - Battery with discharging and charging capability. - AC Loads - The grid/microgrid model must: - Offer fault capability - Offer islanded mode capability - Be controllable through a user-friendly GUI. - Be open for modification by the user. - The DER models must - Offer fault capability - Be selected and configured through a GUI. - Be based on MATLAB/Simulink/Simscape Power Systems - Be open for modification by the user. Note: Integrated renewable energy module should include real-time network simulator (RTNS) to allow simulating a real network and investigating real models. In general, the module should allow a fully controlled (based on voltage and frequency) low voltage grid, fully controlled emulators, fully instrumented equipment and Software programs. | 1 |
| Software license | Software license to run the models MATLAB/Simulink. | 1 |
| Distributed Energy Resources (DER) Emulator | - Minimum 5 kVA - Voltage range of 380/220 V three/single phase system - 100 % sinking capability (four-quadrant operation) - Maximum Total harmonic distortion (THD) of 0.5 % - Feedback of three voltages and three current measurements to real-time network simulator. - Dynamic response less than 5 µs. | 3 |
| Grid Emulator PHIL | - Minimum 5 kVA. - Voltage range of 208 - 253 Vac per phase. - 100% sinking capability (four-quadrant operation). - Minimum of 5 kHz bandwidth at -3db. - Maximum Total harmonic distortion (THD) of 0.5 %. - Feedback of three voltages and three current measurements to real-time network simulator (RTNS) - Dynamic response less than 5 µs. - Direct connection to the micro grid Bus (AC). No additional hardware to connect the DER to the 3-phase bus. | 1 |
| Desktop PCs For data acquisition and system monitoring | - Processor – quad core 2.4 GHz+ (i7 series Intel processor or equivalent AMD) - RAM – 16 GB or more - Hard Drive – 256 GB or larger solid-state hard drive Graphics Card – any with Display Port/HDMI - Monitor – 19" widescreen LCD with Display Port/HDMI - Operating System – Windows 10 Professional edition. | 3 |

شروط خاصة للعطاء:

        - كفالة صيانة لمدة 3 سنوات.

        - دعم فني لمدة 24 شهر من تاريخ استلام لجنة الاستلام في الجامعة.

الاسـم :

التوقيع  :

الختـم :